## Slide 1: Grounding

## Slide 2: Lightning will occur, Be Prepared!
Surge suppression works great.
Installations have been highly successful.
ACC MUST also be grounded !!!!!!
Remember Decoder Systems have LESS wire in
the ground!!!!!
Less Copper = Less attraction
to lightning!
Face Pack still running, 0 decoders lost.

## Slide 3
Why Ground?
  Lightning / Surge Protection
    Dissipates excess voltage and protects components
  Electrical Interference
    AC Voltage and DC Voltage don’t like each other !
Grounding Principles

## Slide 4
How do we ground?
  Grounding Rods
    Copper rod vertically installed, Cadwell connection
  Grounding Plates
    Horizontal flat copper plate, contact material
Grounding Principles

## Slide 6: ACC Ground
The green or bare copper safety ground is not required with this UL listed floating ground, double-insulated transformer.
The ACC features a copper earth ground lug, to the immediate right of the transformer assembly. This earth ground connection is isolated from the primary AC power and is used to ground incoming surges from the communications and output valve wires.

## Slide 7: Controller Ground Installation
Use 6AWG Bare Copper Wire From Controller to Grounding Rod in Smooth Sweeping Turns
8’ Grounding Rod and a 4”x96” Grounding Plate Minimum
Perpendicular to Wire Run
Ground Wire Should Not Be in the Same Sleeve as Your Power or 2 Wire
8’ Away From Controller in an Irrigated Area
Do Not Cut Grounding Rods
ASIC.org
paigewire.com/grounding.htm

## Slide 9: Controller Grounding

## Slide 12: Decoder Grounding

## Slide 13: Detail

## Slide 14: Installation of Ground Plate and Ground Rod
Cadweld Advantages
No maintenance after install
No Turns in Direction (less Resistance)
Decrease Ohms in Grounding Systems